Request For Action Number: 13 Project Gamma-ray Large Area Space Telescope (GLAST) System/Instrument: Large Area Telescope (LAT) Review: Critical Design Review (CDR) Date: May 12-16, 2003 Originator: Jim Ryan Sharon Seipel E. Shippey Phone: 301-286-4975 301-286-8147 301-286-4901 Organization: GSFC/543 GSFC GSFC Category: MGSE Title: MGSE Detailed Dimension Study Action Requested: a) Perform detailed dimension study. Crane hook height appears inadequate for installation of ACD: I&T. pg 30 – crane hook height = 134 in. I&T, pg 31 – ACD needs 124 in. 10 in. Lift Fixture Box Beam, pg 32 - -6 in. Difference (including ACD Clearance and Crane Fittings = 4 in. b) Provide information on the clean room entrances and clearances that will exist when equipment (including GSE) is brought in and out. Supporting Rationale: a) Risk of damage to ACD hardware during installation, or inadequate facilities to perform operation. Minimum clearance between the bottom of the ACD and top of tracker recommended to be at least 6 inches. b) Not enough detail presented. Project Response: